## Sheet1
Code name | Unit | Discription | Study Case | Used
Catchments characteristics
num_locations | -- | Number of locations in which the tariffs for water and wastewater are different | Abu Dis, Al Ezaryia, Sawahera and Al Ubeydia are the towns that compose the study area | 4
total_population | inhabitants | Sum of population from the grid file | The population obtained through the sum of inhabitants in each pixel was slightly bigger than the sum of all the population given by WSRC(2018) - 83,500 inhabitants | 84915
water_consumption | m3/day/capita | Average water consumption of population, given for each location | The average water consumption was obtained from WSRC(2018). The average is the real consumption (losses in the system not included) | [0.043, 0.060, 0.078, 0.054]
losses_infiltration | decimals | Percentage of water lost by infiltration, not reaching the wastewater collection system | Same input data from Matano (2017) | 0.1
coef_peak | no units | Hourly peak flow of wastewater generation | Value stablished to design a robust network system, same input data used by Matano (2017) | 2.4
inhabit_per_household | inhab/house | Average number of people living in a household | Average for West Bank cities, given by Pedersen et al (2001) | 6.2
losses_distribution | decimals | Losses of water during the distribution of water from main provider to local provider | Average given by WSRC(2018) for each of the towns | [0.2646, 0.4723, 0.346, 0.195]
losses_transmission | decimals | Losses of water during the transmission of water from sources to points of distribution | Calculated value based on total volume supplied by main provider (PWA) and received volume by local provider (association or municipality) | [0.17, 0.17, 0.17, 0.17]
collection_efficiency | decimals | Percentage of water tariffs effectively paid by the population | Average given by WSRC(2018) for each of the towns | [0.4195, 0.4748, 0.3008, 0.626]
urb_irrig_use_coef | no units | Percentage of water consumption used for irrigation of gardens | Taken from household water use from Nazer et al (2010) | 0.15
Reuse areas assumptions
area_usage_cas | m2/m3.day | Area needed for WWTP construction of CAS type | Based on Sperling and Chernicharo (2005) | 1.028
area_usage_mbr | m2/m3.day | Area needed for WWTP construction of MBR type | Based on Attiogbe (2013) | 0.514
irr_oper_agr | m3/d.m2 | Optimal rate for agriculture irrigation | Calculated based on (FAO, 1992) | 0.092571
irr_oper_urb | m3/d.m3 | Optimal rate for urban irrigation | Calculated based on (Jordan, 2007) | 0.01
nr_reuse_options | no units | Number of options of post usage of the reclaimed water | The reuse options were chosen as agricultural reuse, urban reuse and no reuse (discharge to nature) | 3
no_data_value_land_price | ILS/m³ | Price attributed to parts of region with no data available regarding land price | The no data value of 200 was chosen as it is an average of price in the lower areas in the region (where also there was no data regarding land price) | 200
no_data_value_loc_index | index | Location index attributted to areas out of classified data | The location index of Abu Dis was chosen, since most of the no classified pixels were in the eastern side of town. | 0
ww_treatment_after_discharge | ILS/m3 | Price of wastewater treatment by third part | The average tariff price charged for wastewater treatment in Israel was taken from the value presented by Fernandes (2013) | 3.36
TECHNOLOGY 1 - Conventional Activated Sludge
known_flow_cas_1 | m3/day | Design Capacity of WWTP1 | Private project (Matano, 2017) | 500
known_flow_cas_2 | m3/day | Design Capacity of WWTP2 | Al Bireh WWTP (Matano, 2017) | 5750
known_inv_cost_cas_1 | ILS | Investment cost for WWTP1 | Private project (Matano, 2017) | 2234998
known_inv_cost_cas_2 | ILS | Investment cost for WWTP2 | Al Bireh WWTP (Matano, 2017) | 14426482
known_oem_cost_cas_1 | ILS/year | O&M cost for WWTP1 | Private project (Matano, 2017) | 83942
known_oem_cost_cas_2 | ILS/year | O&M cost for WWTP2 | Al Bireh WWTP (Matano, 2017) | 274417
TECHNOLOGY 2 - Membrane Bioreactor
known_flow_mbr_1 | m3/day | Design Capacity of WWTP1 | Al Tereeh WWTP (Matano, 2017) | 500
known_flow_mbr_2 | m3/day | Design Capacity of WWTP2 | Al Reehan WWTP (Matano, 2017) | 2000
known_inv_cost_mbr_1 | ILS | Investment cost for WWTP1 | Al Tereeh WWTP (Matano, 2017) | 9231225
known_inv_cost_mbr_2 | ILS | Investment cost for WWTP2 | Al Reehan WWTP (Matano, 2017) | 26070705
known_oem_cost_mbr_1 | ILS/year | O&M cost for WWTP1 | Al Tereeh WWTP (Matano, 2017) | 167885
known_oem_cost_mbr_2 | ILS/year | O&M cost for WWTP2 | Al Reehan WWTP (Matano, 2017) | 548834
Sanitation fees
fee_connection | ILS per houshold | Connection fee to the WWTP | The price was assumed taking as references connection rates from Nablus governorate (WSRC, 2018) | 1500
fee_sanitary | ILS/m3 of drinkable water consumed | Fee for collection and treatment of the wastewater | The price was assumed taking as references sanitary fees from Ramallah governorate (WSRC, 2018) | [1.5, 1.5, 1.5, 1.5]
Water tariff
tariff | Average water price (ILS/m3) | Freshwater tariff | Given by WSRC(2018) for each of the towns | [7.08, 6.42, 4.42, 5]
tariff_reclaimed | Average water price of reclaimed water (ILS/m3) | Reclaimed water tariff | Since Palestine does not have many references in reclaimed water selling, the tariff was estimated as half of the price paid for freshwater | [3.54, 3.21, 2.21, 2.5]
Pipe costs for wastewater collection and reuse water distribution network
Pw | Pw | Cost pipe for the transport of wastewater and reclaimed wastewater [ILS/m] | Based on projects from PWA (Matano, 2017) | [227.1, 259.708, 291.12, 326.63, 361.14, 459.67, 529.18, 598.69]
hRan | hRan | highest range value of the length of the pipes per specific diameter [m] | Based on projects from PWA (Matano, 2017) | [50, 150, 400, 700, 1000, 1500, 2200]
Reservoir costs
known_reservoir_volume_1 | m3 | Design Capacity of Reservoir 1 [m3] | Based on projects from PWA (Matano, 2017) | 500
known_reservoir_volume_2 | m3 | Design Capacity of Reservoir 2 [m3] | Based on projects from PWA (Matano, 2017) | 2000
known_inv_cost_reservoir_1 | ILS | Investment cost for Reservoir 1 [ILS] | Based on projects from PWA (Matano, 2017) | 780400
known_inv_cost_reservoir_2 | ILS | Investment cost for Reservoir 2 [ILS] | Based on projects from PWA (Matano, 2017) | 1951000
Fresh water energy and management costs
portion_s1 | % | Portion of water coming from source 1 | Calculated based on data provided by Service Providers | [29, 25, 100, 15]
portion_s2 | % | Portion of water coming from source 2 | Calculated based on data provided by Service Providers | [71, 75, 0, 0]
portion_s3 | % | Portion of water coming from source 3 | Calculated based on data provided by Service Providers | [ 0, 0, 0, 85]
c_prod_s1 | ILS/m3 | Costs related to production of water at source 1 | Calculated based on data provided by Service Providers | [0.84, 0.84, 0.84, 0.84]
c_prod_s2 | ILS/m3 | Costs related to production of water at source 2 | Calculated based on data provided by Service Providers | [4.38, 4.38, 4.38, 4.38]
c_prod_s3 | ILS/m3 | Costs related to production of water at source 3 | Calculated based on data provided by Service Providers | [3.24, 3.24, 3.24, 3.24]
c_tran_s1 | ILS/m3 | Costs related to transmission of water from source 1 to distribution | Calculated based on data provided by Service Providers | [1.04, 1.04, 0.61, 1.28]
c_tran_s2 | ILS/m3 | Costs related to transmission of water from source 2 to distribution | Calculated based on data provided by Service Providers | [0, 0, 0, 0]
c_tran_s3 | ILS/m3 | Costs related to transmission of water from source 3 to distribution | Calculated based on data provided by Service Providers | [0, 0, 0, 0.49]
c_tran_adm | ILS/m3 | Administrative costs regarding transmission from all sources | Provided by PWA | [0.42, 0.42, 0.42, 0.42]
c_dist_staff | ILS/m3 | Distribution costs regarding staff management | Provided by Service Providers | [1.97, 0.66, 0.70, 0.73]
c_dist_energy | ILS/m3 | Distribution costs regarding energy | Provided by Service Providers | [0.01, 0.02, 0.00, 0.00]
c_dist_adm | ILS/m3 | Distribution costs regarding administration | Provided by Service Providers | [1.41, 0.42, 0.15, 0.91]
c_source_substitute | ILS/m4 | Costs that would be saved if reclaimed water is consumed instead of freshwater | Calculated based on data provided by Service Providers | [4.38, 4.38, 1.45, 3.73]
HYDRAULICS
max_slope_area | % | Max slope in the region | Calculated with QGIS | 24.087
diameter | m | Diameter of pipeline | Average from frwater pdipelines resgessds | 0.15
f | no units | Darcy friction factor | Average from freshwater pipelines | 0.025
h_suction | m | Head at suction | Moody diagram | 0
h_outlet | m | Head at outlet of the pipe | Palestinian guidelines (PWA, 2000) | 20
local_losses_coef | decimals | Percentage of local losses | Estimated by calculation | 0.158
h_reservoir | m | height of the reservoir | Assumed | 5
density | kg/m³ | Water density | Water density | 998.21
pump_operation_time | hours/day | Operation time of pump | Assumed | 6
price_average_kwh | ILS/kwh | Average price for each kwh | Calculated based on data provided by NWC | 0.595
fixed_cost | ILS/month | Fixed price paid to energy company | Based on data provided by NWC | 300
tax_percent | decimals | Percentage of taxes charged on the whole value | Based on data provided by NWC | 0.16
Present value analysis coefficients
DR | decimals | Discount rate is the rate of return used in a discounted cash ﬂow analysis to determine the present value of future cash ﬂows | Assumed | 0.0765
n | years | Number of years of project lifetime | Assumed | 20
Watershed delineation coefficients
snap_distance | no units | Pixels to search around | Assumed by fine tuning | 50
flow_threshold | no units | Threshold for flow | Assumed by fine tuning | 1